## TCO Inputs
Released under: FreeBSD
Author: Vasileios Kontorinis (bkontorinis@gmail.com)
Date: 05/16/2012
Comments: If you use these models please cite the paper "Managing Distributed UPS Energy for Effective Power Capping in Data Centers", V.Kontorinis et al. ISCA 2012.
Also send an email to bkontorinis@gmail.com so that we can track who is using the models.
Compatibility: Microsoft Excel v.2007, 2010(Windows), 2011(Mac)
Version: 1.0

Description	Inputs			Estimated Values
Critical capacity (W)	10,000,000		Number of Servers	33300
Average Rack Power (W)	4,000		Number of Servers with oversubscription	36297
Rack Footage (Sqft)	30		Servers per Rack	17
lifetime - DC Depreciation Time (years)	10		Servers per Rack with oversubscription	17
PUE	1.12		Total Racks	2500
Server Cost ($)	1159.99		Total Racks with oversubscription	2500
Server Depreciation Time (years)	4		Average server power	231.25
Server Utilization	45%
Server Peak Power (W)	500.0
Server Idle Power (W)	175
Electricity Cost ($/kWh)	4.70E-02
Peak Power Cost ($/kW)	12
Degree of over-subscription (extra servers)	0%
Level of over-subscription	Rack
Oversubscription Method	Batteries

				TCO	server cost	server peak power	total servers	perf factor	server total perf	perf / TCO	improv perf/TCO
				218,537,331.84	798	300	33,300.00	1.00	33,300.00	1.52E-04	1.00E+00
				203,550,741.20	1159	500	20,000.00	2.00	40,000.00	1.97E-04	1.29

	total cost	power supply (W)					1.665		1.2012012012	1.289640627
machine with CPU only	$798.00	300
http://www.newegg.com/Product/Product.aspx?Item=N82E16883103863

machine with CPU + GPU	$1,159.99	500	configuration	TCO	server cost	server peak power	total servers	perf factor	server total perf	perf / TCO	improv perf/TCO	improv perf
http://www.newegg.com/Product/Product.aspx?Item=N82E16883103853			CPU only server	218,537,331.84	798	300	33,300.00	1.00	33,300.00	1.52E-04	1.00	1.00
			CPU+GPU server	203,550,741.20	1159	500	20,000.00	1.00	20,000.00	9.83E-05	0.64	0.60
				203,550,741.20	1159	500	20,000.00	2.00	40,000.00	1.97E-04	1.29	1.20
				203,550,741.20	1159	500	20,000.00	3.00	60,000.00	2.95E-04	1.93	1.80
				203,550,741.20	1159	500	20,000.00	4.00	80,000.00	3.93E-04	2.58	2.40
				203,550,741.20	1159	500	20,000.00	5.00	100,000.00	4.91E-04	3.22	3.00
				203,550,741.20	1159	500	20,000.00	6.00	120,000.00	5.90E-04	3.87	3.60
				203,550,741.20	1159	500	20,000.00	7.00	140,000.00	6.88E-04	4.51	4.20
				203,550,741.20	1159	500	20,000.00	8.00	160,000.00	7.86E-04	5.16	4.80
			Performance improvement of CPU+GPU server vs CPU server / Server performance factor / Performance Improvement	203,550,741.20	1159	500	20,000.00	9.00	180,000.00	8.84E-04	5.80	5.41
				203,550,741.20	1159	500	20,000.00	10.00	200,000.00	9.83E-04	6.45	6.01

Comparision between CPU vs CPU+GPU server classes / Server performance factor / Perf / TCO improvement

## TCO Advanced Inputs
Legend
per watt
per Sqft
per Rack
Materials	Mat_
Labor	Lab_
Engineering	Eng_

	Cost per (Watt/Sqft/rack)		Oversubscription scaling	Oversubscription Factor		TCO($)	TCO with oversubscription($)
Mat_UPS_perWatt	0.23		Scales with Critical capacity	1		2,300,000	2,300,000
Mat_Battery_perWatt	0.15		Scales with Critical capacity	1		1,500,000	1,500,000
Lab_UPSBattery_perWatt	0.10		Scales with Critical capacity	1		1,000,000	1,000,000
Eng_UPS_perWatt	0.20		Scales with Critical capacity	1		2,000,000	2,000,000

Mat_Generator_perWatt	0.45		Scales with Critical capacity	1		12,150,000	12,150,000
Eng_Generator_perWatt	0.07		Scales with Critical capacity	1		1,890,000	1,890,000
Lab_Generator_perWatt	0.10		Scales with Critical capacity	1		2,700,000	2,700,000

Mat_BackRoomSwitchGear_perWatt	0.23		Scales with Critical capacity	1		2,300,000	2,300,000
Lab_BackRoomSwitchGear_perWatt	0.10		Scales with Critical capacity	1		1,000,000	1,000,000
Eng_BackRoomSwitchGear_perWatt	0.08		Scales with Critical capacity	1		800,000	800,000

Mat_PowerDistributionUnits_perWatt	0.20		Scales with Critical capacity	1		2,000,000	2,000,000
Lab_PowerDistributionUnits_perWatt	0.10		Scales with Critical capacity	1		1,000,000	1,000,000
Eng_PowerDistributionUnits_perWatt	0.14		Scales with Critical capacity	1		1,400,000	1,400,000

Mat_Cooling_perWatt	0.70		Scales with Critical capacity	1		8,400,000	8,400,000
Lab_Cooling_perWatt	0.40		Scales with Critical capacity	1		4,800,000	4,800,000
Eng_Cooling_perWatt	0.15		Scales with Critical capacity	1		1,800,000	1,800,000

Mat_FireDetectionSuppression_perSqft	40		Scales with Critical capacity	1		3,000,000	3,000,000
Lab_FireDetectionSuppression_perSqft	10		Scales with Critical capacity	1		750,000	750,000
Eng_FireDetectionSuppression_perSqft	4		Scales with Critical capacity	1		300,000	300,000

Mat_RaisedFloor_perSqft	15		Scales with Critical capacity	1		1,125,000	1,125,000
Lab_RaisedFloor_perSqft	15		Scales with Critical capacity	1		1,125,000	1,125,000
Eng_RaisedFloor_perSqft	7		Scales with Critical capacity	1		525,000	525,000

Eng_GeneralBuilding_perSqft	15		Scales with Critical capacity	1		1,125,000	1,125,000

Mat_RackEnclosure_perRack	2000		Scales with Critical capacity	1		5,000,000	5,000,000
Mat_RackPowerDistributionWhips_perRack	800		Scales with Critical capacity	1		2,000,000	2,000,000
Lab_RackPowerDistributionWhips_perRack	200		Scales with Critical capacity	1		500,000	500,000
Mat_RackDataCable_perRack	75		Scales with Critical capacity	1		187,500	187,500
Lab_RackDataCable_perRack	125		Scales with Critical capacity	1		312,500	312,500

Mat_SystemMonitoringCost_perSqft	6.75		Scales with Critical capacity	1		506,250	506,250
Mat_InternalExternalProjectMgmt_perSqft	26		Scales with Critical capacity	1		1,950,000	1,950,000
Mat_SpaceLeasing_perSqft	10		Scales with Critical capacity	1		7,500,000	7,500,000
Mat_RaisedFloorCleaning_perSqft	1		Scales with Critical capacity	1		750,000	750,000
Mat_RoomCleaning_perSqft	0.75		Scales with Critical capacity	1		562,500	562,500
Mat_CoolingService_perWatt	0.09		Scales with Critical capacity	1		10,800,000	10,800,000
Mat_UPSBatteryService_perWatt	0.05		Scales with Critical capacity	1		5,000,000	5,000,000
Mat_GeneratorService_perWatt	0.02		Scales with Critical capacity	1		5,400,000	5,400,000
Mat_AncillaryService_perWatt	0.01		Scales with Critical capacity	1		1,500,000	1,500,000
Mat_PowerDistributionUnitsService_perWatt	0.01		Scales with Critical capacity	1		1,000,000	1,000,000
Lighting_WattsperSqft	2		Scales with Critical capacity	1		609,120	609,120
Electrical Substation Cost			Scales with Critical capacity	1		1,860,000	1,860,000

CracSizingvsLoad	1.2				Total	100,427,870
GeneratorSizingvsLoad	2.7

Costs grouped according to how they scale
per watt	70,740,000
per sqft	19,218,750
per rack	8,000,000
lighting	609,120

## TCO Outputs
Total Cost of Ownership NO Oversubscription (Distributed LA UPS)					Total Cost of Ownership WITH Oversubscription
	TCO	TCO/Month	TCO/Month/server	Trend with server oversubscription			TCO oversub.	TCO/Month	TCO/Month/server
Facility Space	11,625,000	96,875	2.91	Decreasing		Facility Space	11,625,000.00	96,875	2.67
UPS	532,800	4,440	0.13	Constant		UPS LFP	456,000	3,800	0.10
Power Infrastructure	20,310,000	169,250	5.08	Decreasing		Power Infrastructure	20,310,000.00	169,250	4.66
Cooling Infrastructure	8,400,000	70,000	2.10	Decreasing		Cooling Infrastructure w PCM	8,700,000.00	72,500	2.00
Rest	30,671,250	255,594	7.68	Decreasing		Rest	30,671,250.00	255,594	7.04
DC opex	25,621,620	213,514	6.41	Decreasing		DC opex	25,621,620.00	213,514	5.88
Server Depreciation	66,433,500	553,613	16.63	Constant		Server Depreciation	72,412,515.00	603,438	16.63
Server Opex	3,321,675	27,681	0.83	Constant		Server Opex	3,620,625.75	30,172	0.83
PUE overhead	5,530,874	46,091	1.38	Constant		PUE overhead	5,633,508.55	46,946	1.29
Utility Energy	31,705,013	264,208	7.93	Constant		Utility Energy	34,558,464.44	287,987	7.93
Utility Peak	14,385,600	119,880	3.60	Decreasing		Utility Peak	14,385,600.00	119,880	3.30
total	218,537,332	1,821,144	54.69			total	227,994,584	1,899,955	52.34

				Savings	4.29%
	Relative TCO Breakdown		Relative TCO/server Breakdown				Relative Breakdown		Relative TCO/server Breakdown
Facility Space	5.32%		5.32%			Facility Space	5.32%		4.88%
UPS	0.24%		0.24%			UPS	0.21%		0.19%
Power Infrastructure	9.29%		9.29%			Power Infrastructure	9.29%		8.53%
Cooling Infrastructure	3.84%		3.84%			Cooling Infrastructure w PCM	3.98%		3.65%
Rest	14.03%		14.03%			Rest	14.03%		12.88%
DC opex	11.72%		11.72%			DC opex	11.72%		10.76%
Server Depreciation	30.40%		30.40%			Server Depreciation	33.14%		30.40%
Server Opex	1.52%		1.52%			Server Opex	1.66%		1.52%
PUE overhead	2.53%		2.53%			PUE overhead	2.58%		2.36%
Utility Energy	14.51%		14.51%			Utility Energy	15.81%		14.51%
Utility Peak	6.58%		6.58%			Utility Peak	6.58%		6.04%
				Savings	-4.33%		4.29%
total	100.00%		100.00%			total	104.33%		100.00%

			TCO / server breakdown WITH PCM

	Trend with server oversubscription
Decreasing	47.24%
Constant	46.17%

				TCO / server breakdown NO PCM

## Oversubscription with batteries
Description	Inputs				Estimated					Hour	No Shaving	With Shaving
				Battery depr. time (months)	100.0					1	270.0	218.2
Battery Type	LFP				Imax (A)	20.0					2	270.0	218.2
Battery Voltage	12					3	270.0	218.2
Sever PSU efficiency	80%					4	270.0	218.2
				No shaving	With Shaving					5	223.5	234.4
Worload Specific					High Pulse Height	270.0	218.2					6	223.5	234.4
Peak Pulse Width (h)	4				Low Pulse Height	223.5	234.4					7	223.5	234.4
Peak Pulse Height	90%					8	223.5	234.4
Targeted Peak Reduction	19.2%				Max Peak Reduction	14.2%					9	223.5	234.4
Discharges per day	1					10	223.5	234.4
				Required Battery Capacity (Ah)	32.6					11	223.5	234.4
Battery Type Specific					UPS cost per server ($)	163.2					12	223.5	234.4
Battery Cost ($/Ah)	5				UPS depreciation / month ($)	1.6					13	223.5	234.4
Peukert's exponent	1.05				Allowed Oversubscription	23.8%					14	223.5	234.4
DoD goal	60%					15	223.5	234.4
Service life (months)	120					16	223.5	234.4
Battery Efficiency	95%			Hours of the day / Server Power (W)					17	223.5	234.4
				18	223.5	234.4
DoD	Rech.cycles					19	223.5	234.4
10%	100000					20	223.5	234.4
20%	40000					21	223.5	234.4
30%	10000					22	223.5	234.4
40%	6000					23	223.5	234.4
50%	4000					24	223.5	234.4
60%	3000
70%	2000
80%	1700
90%	1200
100%	1000

Analysis
Capacity Size Limit (Ah)	40
		Peak Width
	32.6	0.5	1	2	4	8	16
Targeted Peak Reduction	5.0%	1.5	2.8	5.5	10.6	20.5	39.6
	10.0%	2.8	5.5	10.6	20.5	39.6	76.6
	14.2%	4.2	8.0	15.6	30.1	58.3	112.7
	14.2%	5.3	10.3	19.9	38.5	74.6	144.3
	14.2%	5.3	10.3	19.9	38.5	74.6	144.3

## Validation
APC Calculator -- VALIDATION
PowerEQ	22,250,000
CoolingEQ	8,400,000
EngInstLab	23,027,500
Service	23,700,000
RacksEnclos	5,187,500
Space	12,937,500
SysMon	506,250
ProjMan	1,950,000
Lighting	609,120

Total infrastructure costs (no Lighting)	97,958,750

Infrastructure costs+ Dist.UPS + Substation Cost	96,231,870

## Utils
Oversubscription Level Options				License Information:
Rack				Copyright (c) 2012, Vasileios Kontorinis
PDU				All rights reserved.
Cluster
				Redistribution and use in source and binary forms, with or without modification, are permitted provided that the following conditions are met:
Oversubscription Scaling Options
Scales with Critical capacity				Redistributions of source code must retain the above copyright notice, this list of conditions and the following disclaimer.
Scales with Server Power				Redistributions in binary form must reproduce the above copyright notice, this list of conditions and the following disclaimer in the documentation and/or other materials provided with the distribution.
Custom				THIS SOFTWARE IS PROVIDED BY THE COPYRIGHT HOLDERS AND CONTRIBUTORS "AS IS" AND ANY EXPRESS OR IMPLIED WARRANTIES, INCLUDING, BUT NOT LIMITED TO, THE IMPLIED WARRANTIES OF MERCHANTABILITY AND FITNESS FOR A PARTICULAR PURPOSE ARE DISCLAIMED. IN NO EVENT SHALL THE COPYRIGHT HOLDER OR CONTRIBUTORS BE LIABLE FOR ANY DIRECT, INDIRECT, INCIDENTAL, SPECIAL, EXEMPLARY, OR CONSEQUENTIAL DAMAGES (INCLUDING, BUT NOT LIMITED TO, PROCUREMENT OF SUBSTITUTE GOODS OR SERVICES; LOSS OF USE, DATA, OR PROFITS; OR BUSINESS INTERRUPTION) HOWEVER CAUSED AND ON ANY THEORY OF LIABILITY, WHETHER IN CONTRACT, STRICT LIABILITY, OR TORT (INCLUDING NEGLIGENCE OR OTHERWISE) ARISING IN ANY WAY OUT OF THE USE OF THIS SOFTWARE, EVEN IF ADVISED OF THE POSSIBILITY OF SUCH DAMAGE.

Oversubscription Method
Batteries
Other

Battery Type
LFP
LA

	LFP	LA
Battery Cost ($/Ah)	5	2
Peukert's exponent	1.05	1.15
DoD goal	60%	40%
Service life (months)	120	48
Battery Efficiency	95%	75%

DoD	LFP rech.cycles	LA rech.cycles
10%	100000	5000
20%	40000	2800
30%	10000	1860
40%	6000	1300
50%	4000	1000
60%	3000	830
70%	2000	650
80%	1700	500
90%	1200	410
100%	1000	330

## Server Power
Inlet Temperature (F)		Power		Inlet Temperature (In Centigrade)	Normzlied Server Power
62.5		360		17	86
66		361		19	86
70		363		21	86
74		366		23	87
77		370		25	88
81		378		27	90
84		390		29	93
88		403		31	96
90		420		32	100
94		440		34	105

		Normalized Power vs Temperature